## Plattenwärmeübertrager
Parameters | Symbol | Value | Dimensions
Flow Condition | fc | counterflow | - |  | counter-current
Medium | m | water | -
Chevron Angle | beta | 45 | ° |  | 45
No. of plates | Nt | 22 | - |  | 22
No. Of passes | Np | 1 | - |  | 1
Plate Thickness | s | 0.0006 | m |  | 0.006
Horizontal plate width | Lw | 0.119 | m |  | 1.19
Vertical port length | Lv | 0.243 | m |  | 2.43
Horizontal port width | Lh | 0.072 | m |  | 0.72
compressed plate length | Lc | 0.05328 | m |  | 0.5328
Port diameters | Dp | 0.024 | m |  | 0.24
thermal Conductivity plate (Stainless Steel) | k_steel | 16.5 | W /mK |  | 16.5
Allowable pressure drop primary circuit | PD_Design_prim | 15 | kPa |  | 15
Allowable pressure drop secondary circuit | PD_Design_sec | 15 | kPa |  | 15
Heating load | Q | 43000 | W |  | 43000
Total effective area | A_tot | 0.62 | m2 |  | 0.62
Inlet Temperature primary circuit | T1 | 393.15 | K | 120 | 393.15 | 363.15
Outlet Temperature primary circuit | T2 | 333.15 | K | 60 | 333.15
Inlet Temperature secondary circuit | t1 | 328.15 | K | 55 | 328.15
Outlet Temperature secondary circuit | t2 | 343.15 | K | 70 | 343.15
L.Wang

## Rohrbündelwärmeübertrager
Parameters | Symbol | Value | Dimensions
Flow Condition | fc | counterflow | - |  | counter-current
Medium | m | water | -
Chevron Angle | beta | 45 | ° |  | 45
No. of plates | Nt | 22 | - |  | 22
No. Of passes | Np | 1 | - |  | 1
Plate Thickness | s | 0.006 | m |  | 0.006
Horizontal plate width | Lw | 1.19 | m |  | 1.19
Vertical port length | Lv | 2.43 | m |  | 2.43
Horizontal port width | Lh | 0.72 | m |  | 0.72
compressed plate length | Lc | 0.533 | m |  | 0.5328
Port diameters | Dp | 0.24 | m |  | 0.24
thermal Conductivity plate (Stainless Steel) | k_steel | 16.5 | W /mK |  | 16.5
Allowable pressure drop primary circuit | PD_Design_prim | 15 | kPa |  | 15
Allowable pressure drop secondary circuit | PD_Design_second | 15 | kPa |  | 15
Heating load | Q | 43000 | W |  | 43000
Total effective area | A_tot | 0.62 | m2 |  | 0.62
Inlet Temperature primary circuit | T1 | 393.15 | K | 120 | 393.15 | 363.15
Outlet Temperature primary circuit | T2 | 333.15 | K | 60 | 333.15
Inlet Temperature secondary circuit | t1 | 328.15 | K | 55 | 328.15
Outlet Temperature secondary circuit | t2 | 343.15 | K | 70 | 343.15

## Vergleich Methodiken
|  | Ergebnis Wärmeübertrager Swep | Ergebis Rechnung Paper | Ergebis Rechnung Paper | Ergebis Rechnung paper Reich TU Graz | Ergebnis Wärmeübertrager Swep | Ergebnis Wärmeübertrager Swep | Ergebis Rechnung buch L.Wang | Ergebis Rechnung buch Kacak | Ergebis Rechnung buch Kacak version 2 aus paper | Ergebis Rechnung buch Thulkunam | Ergebis Rechnung buch Sekulölic | Ergebis Rechnung buch Hesselgreaves
| Dimensions | Wert | Wert | Wert | Wert |  |  | Wert | Wert | Wert | Wert | Wert | Wert
Compressed length | m |  | 0.05528 | 0.05328 | 0.05528 | compressed plate length | ? | 0.05528 | 0.05528 | 0.05528 | 0.05528 | 0.05528
Heat load | kW | 44.78 | 41.976 | 43.728 |  | Pitch | ? | 0.0025127 | 0.0025127 | 0.0025127 | 0.0025127 | 0.0025127
Inlet temperature primary | K | 120 | 120 | 120 |  | mean channel spacing | ? | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127
Outlet temperature primary | K | 330.65 | 330.65 | 330.65 |  | channel flow Area | ? | 0.00022761 | 0.00022761 | 0.00022761 | 0.00022761 | 0.00022761
Inlet temperature secondary | K | 328.15 | 328.15 | 328.15 |  | enlargment factor | ? | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895
Outlet temperature secondary | K | 343.77 | 343.77 | 343.77 |  | hydraulic diameter | ? | 0.003216 | 0.003216 | 0.003216 | 0.003216 | 0.003216
Mean temperature difference | K | 15.78 | 15.78 | 15.78 |  | flow channel velocity hot streams | 0.078 | 0.070837 | 0.070837 | 0.070837 | 0.070837 | 0.070837
Re primary |  | 944.4 | 690.0048 | 690.0048 | 710 | flow channel velocity cold streams | 0.281 | 0.28023 | 0.28023 | 0.28023 | 0.28023 | 0.28023
Re secondary |  | 2461 | 1974.83 | 1974.83 | 2800 | mass velocity per channel hot streams | ? | 68.4431 | 68.4431 | 68.4431 | 68.4431 | 68.4431
Nu primary |  |  | 35.35 | 35.35 | 15.2701 | mass velocity per channel cold streams | ? | 275.103 | 275.103 | 275.103 | 275.103 | 275.103
Nu secondary |  |  | 80.38 | 80.38 | 30.3245 | port area |  | 0.00045239 | 0.00045239 | 0.00045239 | 0.00045239 | 0.00045239
Film coefficient primary | W/m²,°C | 7490 | 7415.5 | 7785 | 3100.3022 | mass velocity per port hot streams |  | 361.582 | 361.582 | 361.582 | 361.582 | 361.582
Film coefficient secondary | W/m²,°C | 16900 | 16422.8 | 17242.3 | 6156.7833 | mass velocity per port cold streams |  | 1453.36 | 1453.36 | 1453.36 | 1453.36 | 1453.36
O.H.T.C. (available | W/m²,°C | 4600 | 4308 | 4488 |  | port channel velocity hot streams | 0.39 | 0.37423 | 0.37423 | 0.37423 | 0.37423 | 0.37423
O.H.T.C. fouled | W/m²,°C |  | 3675 | 3805 |  | port channel velocity hot streams | 1.54 | 1.4805 | 1.4805 | 1.4805 | 1.4805 | 1.4805
friction factor prim |  |  | 0.3347 | 0.3347 |  | Prandl No hot streams |  | 1.9889 | 1.9889 | 1.9889 | 1.9889 | 1.9889
friction factor sec |  |  | 0.1979 | 0.1979 |  | Prandl No cold streams |  | 2.855 | 2.855 | 2.855 | 2.855 | 2.855
Pressure drop - total* primary | kPa | 1.28 | 0.33 | 0.368 |  | Reynolds No hot streams | 944.4 | 690.005 | 690.005 | 690.005 | 690.005 | 690.005
- in ports primary | kPa | 0.0696 | 0.0947 | 0.094 |  | Reynolds No cold streams | 2461 | 1974.83 | 1974.83 | 1974.83 | 1974.83 | 1974.83
- in channels primary | kPa | 1.2104 | 0.236 | 0.273 |  | Nusselt No hot streams |  | 29.4596 | 29.4596 | 11.5181 | 36.7263 | 53.4665
Pressure drop - total* secondary | kPa | 14.7 | 3.853 | 4.22 |  | Nusselt No cold streams |  | 66.9905 | 66.9905 | 28.7949 | 83.5148 | 111.342
- in ports secondary | kPa | 1.11 | 1.506 | 1.506 |  | heat transfer coeff hot streams | 7490 | 6179.61 | 6179.61 | 2416.1 | 7703.91 | 11215.4
- in channels secondary | kPa | 13.59 | 2.346 | 2.716 |  | heat transfer coeff cold streams | 16900 | 13685.7 | 13685.7 | 5882.6 | 17061.5 | 22746.4
Channel velocity primary | m/s | 0.078 | 0.0708 | 0.0744 | 0.071 | clean heat transfer coeff | 4600 | 3686.56 | 3686.56 | 1612.26 | 4448.81 | 5900.07
Channel velocity secondary | m/s | 0.281 | 0.28 | 0.29 | 0.28 | fouled heat transfer coeff |  | 3212.8 | 3212.8 | 1514.59 | 3776.73 | 4773.51
Port velocity primary | m/s | 0.39 | 0.3742 | 0.3742 | 0.37 | heat duties cleaned | 44780 | 35917.9 | 35917.9 | 15708.1 | 43344.3 | 57483.9
Port velocity secondary | m/s | 1.54 | 1.48 | 1.48 | 1.48 | heat duties fouled |  | 31302 | 31302 | 14756.5 | 36796.3 | 46507.9
[6 empty] | Reserve | 0 | -16.47 | -16.47 | -63.4694 | 0.8008 | 33.6834
Reserve | % | 4.1395 | -2.3814 | 1.693 |  | pressure drop port hot stream | 0.0696 | 101.486 | 94.7206 | 94.7206 | 101.486 | 101.486
[6 empty] | pressure drop channel hot stream | 1.21 | 3004.14 | 2.7465 | 72.5416 | 274.648 | 491.77
[6 empty] | total pressure drop hot stream | 1.28 | 3105.62 | 3.6937 | 167.262 | 376.135 | 593.256
[6 empty] | pressure drop port cold stream | 1.11 | 1613.71 | 15.0613 | 1506.13 | 1613.71 | 1613.71
[6 empty] | pressure drop channel cold stream | 13.59 | 62131 | 3516.58 | 822.876 | 3516.58 | 6011.89
[6 empty] | total pressure drop cold stream | 14.7 | 63744.7 | 5022.71 | 2329.01 | 5130.29 | 7625.61
[6 empty] | NTU |  | 0.83028 | 0.83028 | 0.36311 | 1.0019 | 1.3288
[6 empty] | Verhältnis der Wärmekapazitätsströme R |  | 4.0013 | 4.0013 | 4.0013 | 4.0013 | 4.0013
[6 empty] | Heat duty new |  | 41885.6 | 41885.6 | 32404.8 | 43041.1 | 44095.4
The pressure drop in the manifolds and ports should be kept as low as
possible (generally <10%, but may be as high as 25 to 30% or higher in some designs).

## Kacak Methods
| Dimensions | Wert | Wert | Wert
Compressed length | m |  | 0.05528 | 0.05328
Heat load | kW | 44.78 | 41.976 | 43.728
Inlet temperature primary | K | 120 | 120 | 120
Outlet temperature primary | K | 330.65 | 330.65 | 330.65
Inlet temperature secondary | K | 328.15 | 328.15 | 328.15
Outlet temperature secondary | K | 343.77 | 343.77 | 343.77
Mean temperature difference | K | 15.78 | 15.78 | 15.78
Re primary |  | 944.4 | 690.0048 | 690.0048
Re secondary |  | 2461 | 1974.83 | 1974.83
Nu primary |  |  | 35.35 | 35.35
Nu secondary |  |  | 80.38 | 80.38
Film coefficient primary | W/m²,°C | 7490 | 7415.5 | 7785
Film coefficient secondary | W/m²,°C | 16900 | 16422.8 | 17242.3
O.H.T.C. (available | W/m²,°C | 4600 | 4308 | 4488
O.H.T.C. fouled | W/m²,°C |  | 3675 | 3805
friction factor prim |  |  | 0.3347 | 0.3347
friction factor sec |  |  | 0.1979 | 0.1979
Pressure drop - total* primary | kPa | 1.28 | 0.33 | 0.368
- in ports primary | kPa | 0.0696 | 0.0947 | 0.094
- in channels primary | kPa | 1.2104 | 0.236 | 0.273
Pressure drop - total* secondary | kPa | 14.7 | 3.853 | 4.22
- in ports secondary | kPa | 1.11 | 1.506 | 1.506
- in channels secondary | kPa | 13.59 | 2.346 | 2.716
Channel velocity primary | m/s | 0.078 | 0.0708 | 0.0744
Channel velocity secondary | m/s | 0.281 | 0.28 | 0.29
Port velocity primary | m/s | 0.39 | 0.3742 | 0.3742
Port velocity secondary | m/s | 1.54 | 1.48 | 1.48
Reserve | % | 4.1395 | -2.3814 | 1.693

## Tabelle2
compressed plate length | 0.05328
Pitch | 0.0024218 | 0.0024218
mean channel spacing | 0.0018218 | 0.0018218
channel flow Area | 0.0002168 | 0.0002168
enlargment factor | 1.1895 | 1.1895
hydraulic diameter | 0.0030631 | 0.0030631
flow channel velocity hot streams | 0.074372 | 0.077767
flow channel velocity cold streams | 0.29422 | 0.30616
mass velocity per channel hot streams | 71.8585 | 75.1384
mass velocity per channel cold streams | 288.831 | 300.5536
port area | 0.00045239 | 0.00045239
mass velocity per port hot streams | 361.582 | 376.6479
mass velocity per port cold streams | 1453.36 | 1513.4284
port channel velocity hot streams | 0.37423 | 0.38982
port channel velocity hot streams | 1.4805 | 1.5416
Prandl No hot streams | 1.9889 | 1.9889
Prandl No cold streams | 2.855 | 2.8551
Reynolds No hot streams | 690.005 | 718.755
Reynolds No cold streams | 1974.83 | 2056.4611
Nusselt No hot streams | 11.5181 | 36.3268
Nusselt No cold streams | 28.7949 | 82.5888
heat transfer coeff hot streams | 2536.67 | 8000.3573
heat transfer coeff cold streams | 6176.14 | 17714.2163
clean heat transfer coeff | 1687.78 | 4591.1598
fouled heat transfer coeff | 1581.04 | 3878.8272
heat duties cleaned | 16443.9 | 55630.2387
heat duties fouled | 15403.9 | 46999.0354
Reserve | -61.7584 | 29.3726
pressure drop port hot stream | 94.7206 | 102.7785 | Pressure drop - total* primary | kPa | 1.28
pressure drop channel hot stream | 83.952 | 796.7853 | - in ports primary | kPa | 0.0696
total pressure drop hot stream | 178.673 | 899.5638 | - in channels primary | kPa | 1.2104
pressure drop port cold stream | 1506.13 | 1633.2136 | Pressure drop - total* secondary | kPa | 14.7
pressure drop channel cold stream | 952.31 | 11019.1101 | - in ports secondary | kPa | 1.11
total pressure drop cold stream | 2458.44 | 1573995959.1573 | - in channels secondary | kPa | 13.59
NTU | 0.38012
Verhältnis der Wärmekapazitätsströme R | 4.0013
Heat duty new | 33070.9
Inner Fouling 2e-05
Outer Fouling 2e-05